## Tab A Description
Work Approval Form (WAF)
Cost Center: | 1170
Job Number: | 5500 (Covers elements 5200 - 5500)
Job Title: | NSTX Center Stack Upgrade - Power System
Job Manager: | S. Ramakrishnan
Description:
The Center stack upgrade entails the TF feed to be 1kV, 129.8kA for 7.45 seconds every 2400 seconds. Design shall be such that the pulse period can be reduced to 1200 seconds. This requires complete redesign of the TF power system. Replacement of the fault detector (FD) and the Firing generator (FG) is required for fast and reliable response to fault conditions. The HCS will be upgraded with a PLC. The OH power supply will be also redesigned to have the capabiity of 8kV, +/-24kA; the FD and FG of the OH system will also be changed. OH CLRs will be replaced with calculated optimum requirements. A Digital Coil Protection (DCP) System will be designed and implemented.
Schedule:
Refer to Primavera Data-Base
Approvals:
___________________________________________________________
Job Manager
___________________________________________________________
Project Manager
__________________________________________________________
Engineering Department Head

## Tab B Cost Estimate
Cost Center: | 1170
Job Number: | 5500 (Covers elements 5200 - 5500)
Job Title: | NSTX Center Stack Upgrade - Power System
Job Manager: | S. Ramakrishnan
NSTX CENTER STACK UPGRADE - PS CHANGES 130kA part capability 8 parallels ------- 091509 | [12 empty] | M&S | [5 empty] | Design/ Procurement |  | Installation |  |  |  | Commissioning |  |  | Line Total | Names of req'd skills if known | Basis of Estimate Category
1. TF WILL BE PULSED AT 129.778kA FOR 7.6 SECONDS EVERY 2400 SECONDS | [5 empty] | Start date | Finish date | Mult | Qty | excl factor | Qnty | Units | Qty | Units | Unit Cost | Cost | Spare Units | Spare Cost | EEEM | Dm | EEEM | EESM | EETB | SC | EEEM | EESM | EETB
[15 empty] | (k$/unit) | ($K) |  | ($K) | (md) | (md) | (md) | (md) | (md) | ($K) | (md) | (md) | (md) | ($K)
51- AC Power | 62.5955
| 511- Experimental AC Power | 62.5955
|  |  | Grounding |  | Misc. grounding |  |  | 1 |  | 1 |  |  | 1 | lot | 1 | 3 |  | 1 | 1 | 2 | 1 | 2 | 5 |  | 1 | 2 | 2 | 19.1942 |  | 2
|  |  | D-site Pulsed AC Power Distribution |  | Lockouts/protection/reactivate |  |  | 1 |  | 1 |  |  | 1 | lot | 5 | 5 |  | 0 | 3 | 3 | 2 | 8 | 10 |  | 3 | 3 | 5 | 43.4013 |  | 2
52 - AC/DC Converters | 48.8921
| 521 - Reactivation Converters | 48.8921 | [5 empty] | 1 |  | 1
|  |  | Coil Power Supplies | Transrex PS Maintenance | Reactivation |  |  | 1 |  | 1 |  |  | 12 | PSS | 1 | 12 | 1 | 1 | 0.5 | 1 | 0 | 0 | 0 |  | 5 | 10 | 20 | 48.8921 |  | 2
53 - DC Systems | 1689.1339
| 531-FCPC DC Changes | 1689.1339
| 531.1 PF1a Changes | 255.3234
|  |  | NSTX PF1a Changes | Design & Supervision |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | 10 | 20 | 5 | 5 | 5 |  | 5 | 5 | 10 | 67.7524 |  | 2
|  |  | NSTX PF1a Changes | Task of removing Ripple reactors & Recabling |  |  |  | 1 |  | 1 |  |  |  | 0 | 1 | 1 |  | 0 | 3 | 4 | 2 | 5 | 20 | 50 | 1 | 1 | 2 | 96.5433 |  | 4
|  |  | NSTX PF1a Changes | task of TF reactor enclosures |  |  |  | 1 |  | 1 |  |  |  | 0 | 1 | 20 |  | 0 | 4 | 4 | 2 | 15 | 30 | 10 | 1 | 1 | 2 | 91.0277 |  | 4
531 - FCPC TF DC Systems | 799.8102
| 531.2- TF Changes | 799.8102
|  |  | TF DC Changes FCPC | Design & Supervision |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | 40 | 40 | 5 | 5 | 15 |  | 5 | 5 | 10 | 134.1196 |  | 2
|  |  |  | Materials & Installation | 1000MCM 5kV Cable For PSS |  |  | 1 | 40 | 1 | 100 | ft/PSS | 4500 | ft | 0.03 | 135 |  | 0 | Design/ Procurement EEEM: 5; Design/ Procurement Dm: 5 | 176.8984 |  | 2009-04-06
[5 empty] | Cable Tray in FCPC |  |  | 1 |  | 1 |  |  | 150 | ft | 0.05 | 7.5 |  | 0 | Design/ Procurement EEEM: 2; Design/ Procurement Dm: 2 | 13.7504 |  | 2
[5 empty] | Install Tray in FCPC |  |  | 1 |  | 1 |  |  | 150 | ft | 0.1 | 15 |  | 0 | Design/ Procurement EEEM: 2; Design/ Procurement Dm: 2 | 22.9454 |  | 2
|  |  | NSTX TF Power cabling changes | Task of NSTX TF PS cabling changes |  |  |  | 1 |  | 1 | [5 empty] | 10 |  | 0 | 3 | 4 | 2 | 5 | 40 | 320 | 1 | 1 | 2 | 452.0965 |  | 4
| 531.3- Removing cabling | 89.1873 | Removing cabling | Misc |  |  |  | 1 |  | 1 | [5 empty] | 5 |  | 0 | 3 | 4 | 2 | 5 | 20 | 40 | 1 | 1 | 2 | 89.1873 |  | 4
| 531.4 DC Reactors | 386.9908 | DC Reactors for TF & OH | Design & Specification |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 6; Design/ Procurement Dm: 10 | 17.1512
|  |  |  | Procurement OH Reactors |  |  |  | 1 |  | 1 |  |  | 2 | units | 50 | 100 |  | 0 | [9 empty] | 122.6 |  | 6
|  |  |  | TF reactor Installation |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 |  |  | 5 | 10 | 10 | 20 | 3 | 5 | 5 | 64.0072
|  |  |  | OH Reactor Installation |  |  |  | 1 |  | 1 |  |  |  | 2 | 20 | 40 |  | 0 |  |  | 5 | 10 | 5 | 80 | 3 | 5 | 5 | 183.2324 |  | 6
| 531.5 TA Cabling Changes | 53.0137 | Transition area cabling PF/CHI | Misc |  |  |  | 1 |  | 1 | [5 empty] | 6 |  | 0 | 3 | 4 | 2 | 5 | 10 | 15 | 1 | 1 | 2 | 53.0137 |  | 2
532- TA-NTC DC Systems | 104.8086
104.8086
| 532.1 PCTS Changes |  | PCTS Changes | PCTS Changes |  |  |  | 1 |  | 1 |  |  | 1 |  | 15 | 15 |  | 0 | 3 | 15 | 2 | 10 | 20 | 30 | 1 | 1 | 2 | 104.8086 |  | 2
54 - Control & Protection Systems | 4337.0383
| 541 - Electrical Interlocks | 691.8657
|  |  |  | Design |  |  |  | 1 |  | 1 |  |  | 1 | units | 2 | 2 |  | 0 | Design/ Procurement EEEM: 8; Design/ Procurement Dm: 16; Installation EESM: 5; Installation EETB: 15; Installation SC: 40 | 92.8453 |  | 2
|  |  |  | PLC |  |  |  | 1 |  | 1 |  |  | 1 | units | 98 | 98 |  | 0 | Design/ Procurement EEEM: 180; Design/ Procurement Dm: 40; Installation EESM: 5; Installation EETB: 120 | 495.1836 |  | 4
|  |  |  | Install interlocks/cabling |  |  |  | 1 |  | 1 |  |  | 1 | units | 2 | 2 |  | 0 | Design/ Procurement EEEM: 5; Design/ Procurement Dm: 10; Installation EESM: 5; Installation EETB: 15; Installation SC: 35 | 77.2684 |  | 4
|  |  |  | Test Modified NSTX HCS |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 5; Commissioning EESM: 5; Commissioning EETB: 20 | 26.5684 |  | 2
| 542 - Kirk Key Interlocks | 76.3028
|  |  |  | Kirk Keys |  |  |  | 1 |  | 1 |  |  | 1 | lot | 15 | 15 |  | 0 | 5 | 10 | 2 | 5 | 15 |  | 5 | 5 | 15 | 76.3028 |  | 4
| 543 - Real Time Control | 168.768
|  |  |  | Develop Control Algorithms |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 120 | 168.768 |  | 2
| 544 -PC Link/FD/FG changes | 2643.744
|  |  |  | Control Link/FD/FG Changes | TF wing only |  |  | 1 |  | 1 | [5 empty] | 820 |  | 10 | 450 | 100 | 95 | 10 | 900 | 10 | 80 |  | 60 | 2643.744 |  | 2;6
| 545 - Instrumentation | 577.6401
|  |  | DC Current Transducers (DCCTs) |  |  |  |  | 1 |  | 1 |  |  | 2 | units | 70 | 140 | 0 | 0 | 5 | 10 | 4 | 8 | 20 |  | 3 | 3 | 15 | 234.135 |  | 6
|  |  | DC Current Transducers (DCCTs) |  |  |  |  | 1 |  | 1 |  |  | 8 | units | 10 | 80 | 0 | 0 | 5 | 10 | 4 | 8 | 20 |  | 3 | 3 | 15 | 160.575 |  | 6
|  |  | Signal Conditioning & Associated Cabling |  |  |  |  | 1 |  | 1 |  |  | 1 | lot | 9 | 9 | 0 | 0 | 15 | 10 | 5 | 0 | 20 | 80 | 10 | 5 | 5 | 182.93 |  | 4
| 546 - Coil Protection | 178.7178
|  |  | Overload Protection & Associated Cabling(TF) |  |  |  |  | 1 |  | 1 |  |  | 1 | units | 4 | 4 | 1 | 4 | 50 | 30 | 10 | 20 | 20 |  | 10 | 4 | 10 | 178.7178 |  | 2
55 - System Design and Integration | 612.9047
| 551 - System Design | 442.6844
|  |  | Design Drawings & Drawings changes , as-builts | New drawings & Misc. updates |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 50; Design/ Procurement Dm: 70 | 131.3096 |  | 2
|  |  |  | Analysis |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 70; Installation SC: 15 | 116.838
|  |  | CDR Power system | All power systems |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Design/ Procurement Dm: 15 | 34.1652 |  | 2
|  |  | PDR Power system | All power systems |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Design/ Procurement Dm: 15 | 34.1652 |  | 2
|  |  | FDR D-Site | Transrex D-Site |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Design/ Procurement Dm: 15 | 34.1652 |  | 2
|  |  | FDR Cabling | D site |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Design/ Procurement Dm: 15 | 34.1652 |  | 2
|  |  | Calculations | Calculations - documentation |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Installation SC: 30 | 57.876 |  | 2
| 552 - System Testing | 170.2203
|  |  | Procedures PTPs, ISTPs | New Procedures |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Design/ Procurement Dm: 15 | 34.1652 |  | 2
|  |  |  | DC Circuit Hipots and Impedance Measurements |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 3; Commissioning EETB: 8 | 9.6189 |  | 2
|  |  |  | Electrical Interlock Testing |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 3; Commissioning EETB: 8 | 9.6189 |  | 2
|  |  |  | Kirk Key Interlock Testing |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 2; Commissioning EETB: 3 | 4.8377 |  | 2
|  |  |  | Instrumentation Test & Calibration |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 2; Commissioning EETB: 2 | 4.1627 |  | 2
|  |  |  | Real Time Control System Testing |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Commissioning EEEM: 3; Commissioning EETB: 3 | 6.2441 |  | 2
|  |  |  | Coil Protection System Testing |  |  |  | 1 |  | 1 | [5 empty] | 0 |  | 0 | Design/ Procurement EEEM: 15; Commissioning EEEM: 3; Commissioning EETB: 3 | 27.3401 |  | 2
|  |  |  | Coil Power Supply Dummy Load Testing |  |  |  | 1 |  | 1 |  |  | 10 | PS |  | 0 |  | 0 | 0 |  | 5 |  | 20 |  | 20 | 10 | 20 | 74.2328 |  | 2
|  |  | TOTALS | [12 empty] | 1544.5 |  | 16 | 1156.5 | 501 | 160 | 151 | 1355 | 775 | 183 | 76 | 256 | 6750.5645
[15 empty] | M&S --> | 1893.557 |  | 16 | 1626.5016 | 436.5113 | 225.024 | 182.3234 | 914.5708 | 950.15 | 257.3712 | 91.7654 | 172.7898 | 6766.5645
Notes:
SCOPE COVERED |  |  |  |  | Summary of Basis of Estimate A Work Breakdown Structure has been developed for the project under which the Power System is classified as WBS5. This Cost Estimate has been developed based on the following: • Prior Experience • Similar tasks previously executed • Input from Vendors • Engineering Judgment • Other aspects • Costs are essentially center -of-the-error bars • Areas of risk judged ; constraints noted | [13 empty] | Design/ Procurement EEEM: CATEGORIZATION CODES:
1. TF WILL BE PULSED AT 130kA FOR 7.3 SECONDS EVERY 900 SECONDS | [18 empty] | Design/ Procurement EEEM: 1 - National Standards
2 Sub-contract estimates based on bids and a projected increase of costs | [18 empty] | Design/ Procurement EEEM: 2 - Engineering Judgement/Experience
3. PC LINK CHANGES INCLUDED | [18 empty] | Design/ Procurement EEEM: 3 - Estimates/Data from External Sources (e.g., W7X, ATF, etc.)
4. Cost in 09 Dollars | [18 empty] | Design/ Procurement EEEM: 4 - Previous PPPL/ORNL Experieince (e.g., TFTR, NSTX, PLT, etc.)
5. SCHEDULE WILL AFFECT COST | [18 empty] | Design/ Procurement EEEM: 5 - Prototype Data/Test Results
6 - Catelogue Price/Vendor Quote
7 - Placed Contracts
8 - Actual experience for NCSX Work
9 - Other
FY2009 Hourly Rates
EEEM | 1.4064 | 175.8 | [16 empty] | Installation EEEM: 1321.9182
EESM | 1.2074 | 150.93
EETB | 0.67496 | 84.37 | [15 empty] | ∑MD | Design/ Procurement EEEM: Rate; Design/ Procurement Dm: $K; Installation EEEM: ∑FTE; Installation EESM: Years; Installation EETB: FTE/yr
G&A (MHX) | 1.226 | 1.226 | [13 empty] | cross check | EEEM | 1499.5 | Design/ Procurement EEEM: 1.4064; Design/ Procurement Dm: 2108.8968; Installation EEEM: 6.8159; Installation EESM: 4; Installation EETB: 1.704
DM | 0.87128 | 108.91 | [14 empty] | EESM | 227 | Design/ Procurement EEEM: 1.2074; Design/ Procurement Dm: 274.0889; Installation EEEM: 1.0318; Installation EESM: 2; Installation EETB: 0.51591
[17 empty] | EETB | 1611 | Design/ Procurement EEEM: 0.67496; Design/ Procurement Dm: 1087.3606; Installation EEEM: 7.3227; Installation EESM: 2; Installation EETB: 3.6614
[17 empty] | EADM | 501 | Design/ Procurement EEEM: 0.87128; Design/ Procurement Dm: 436.5113; Installation EEEM: 2.2773; Installation EESM: 3; Installation EETB: 0.75909
[17 empty] | M&S |  | Design/ Procurement Dm: 2843.707

## Tab B-1 Cost Estimate MPS
Cost Center: | 1170
Job Number: | 5500 (Covers elements 5200 - 5500)
Job Title: | NSTX Center Stack Upgrade - Power System
Job Manager: | S. Ramakrishnan
|  |  | TASK DESCRIPTION | [9 empty] | M&S | [5 empty] | Design/ Procurement |  | Installation |  |  |  | Commissioning |  |  | Line Total | No contingency provided |  |  |  | Total Cost | Names of req'd skills if known | Basis of Estimate Category
[6 empty] | Start date | Finish date | Multiplier | Qnty | Units | Qnty | Units | Qnty | Units | Unit Cost | Cost | Spare Units | Spare Cost | EEEM | EASB | EEEM | EESM | EETB | Sub contract | EEEM | EESM | EETB |  | Tech | Cost | Schedule | Total
[15 empty] | (k$/unit) | ($K) |  | ($K) | (md) | (md) | (md) | (md) | (md) | ($K) | (md) | (md) | (md) | ($K) | (%) | (%) | (%) | (%) | ($K)
547 - Digital Coil Protection (DCP)
|  |  | DCP design | Design & Supervision |  |  |  | 1 | [7 empty] | 0 |  | 0 | 95 | 90 | [7 empty] | 224.796 | 0 | 0 | 0 | 0 | 224.796 | Woolley | 2
|  |  |  | Hardware |  |  |  | 1 | [5 empty] | 2 | 140 | 280 |  |  | 2 | 2 |  | 4 | 8 |  |  | 10 | 10 | 377.1726 | 0 | 0 | 0 | 0 | 377.1726 | Lawson | 2
|  |  |  | I&C support | (P.Sichta) |  |  | 1 | [10 empty] | 70 | 0 | [5 empty] | 40 | 5 | 150.1204 | 0 | 0 | 0 | 0 | 150.1204 | Sichta | 2
|  |  |  | Software |  |  |  | 1 | [10 empty] | 140 | 0 | [5 empty] | 50 | 2 | 258.6179 | 0 | 0 | 0 | 0 | 258.6179 | Raki | 2
|  |  |  | Cabling/Raceways |  |  |  | 1 | [5 empty] | 1 | 18 | 18 |  |  |  |  | 12 | 50 | 100 | 25 |  | 2 | 2 | 201.2276 | 0 | 0 | 0 | 0 | 201.2276
| 592 - System Testing | 13.1552 | 13.1552 | [25 empty] | 0 | 0 | 0 | 0
|  |  | Procedures PTPs, ISTPs | Procedures |  |  |  | 1 | [7 empty] | 0 |  | 0 | 2 | 2 | [7 empty] | 5.2277 | 0 | 0 | 0 | 0 | 5.2277
|  |  |  | Pwr Supply PTP |  |  |  | 1 | [16 empty] | 2 | 2 | 4 | 7.9275 | 0 | 0 | 0 | 0 | 7.9275
|  |  | TOTALS | [12 empty] | 298 |  | 0 | 309 | 94 | 12 | 54 | 108 | 25 | 2 | 104 | 23 | 1225.0898 | 0 | 0 | 0 | 0 | 1225.0898
CATEGORIZATION CODES:
1 - National Standards
2 - Engineering Judgement/Experience
3 - Estimates/Data from External Sources (e.g., W7X, ATF, etc.)
4 - Previous PPPL/ORNL Experieince (e.g., TFTR, NSTX, PLT, etc.)
5 - Prototype Data/Test Results
6 - Catelogue Price/Vendor Quote
7 - Placed Contracts
8 - Actual experience for NCSX Work
9 - Other
RATES | [14 empty] | M&S --> | 323
EEEM | 1.421
EESM | 1.203 | [14 empty] | 365.348
EETB | 0.66 | [14 empty] | 30.65
G&A | 1.226
EASB | 1.0132
[27 empty] | EEEM | 323 |  |  |  |  | 454.2672
[27 empty] | EESM(D) | 94 |  |  |  |  | 95.2408
[27 empty] | EESM | 158 |  |  |  |  | 190.7755
|  | FY2009 Hourly Rates | [24 empty] | EETB= | 131 |  |  |  |  | 88.4198
EEEM | 1.4211 | 177.64 | 1.4211 | 1.368 | [22 empty] | M&S | [5 empty] | 395.998
EESM | 1.2028 | 150.35 | 1.2028 | 1.16 | [22 empty] | Total | [5 empty] | 1224.7013
EETB | 0.65952 | 82.44 | 0.65952 | 0.64 | [12 empty] | 1556.6825
G&A (MHX) | 1.226 | 1.281 |  | 1.25
DM | 1.0132 | 126.65 | 1.0132 | 0.99

## Summary
WBS 5 BREAKDOWN WITH COST WITHOUT CONTINGENCY |  |  |  |  | k$ | k$
Ø51 | AC POWER |  |  |  | 62.5955
| Ø511 | Experimental AC Power |  |  |  | 62.5955
Ø52 | AC/DC CONVERTERS |  |  |  | 48.8921
| Ø521 | Reactivate Converters |  |  |  | 48.8921
Ø53 | DC SYSTEMS |  |  |  | 1689.1339
| Ø531 | FCPC DC Systems
|  | Ø531.1 | NSTX PF1a PS loop changes |  |  | 255.3234
|  | Ø531.2 | TF PS Power Cabling/Changes |  |  | 799.8102
|  | Ø531-3 | Removing Cabling |  |  | 89.1873
|  | Ø531.4 | DC Reactors |  |  | 386.9908
|  | Ø531.5 | TA Cabling Changes |  |  | 53.0137
| Ø532 | TA to NTC and NTC changes
|  | Ø532.1 | PCTS Changes |  |  | 104.8086
Ø54 | CONTROL & PROTECTION SYSTEM |  |  |  | 5562.1281
| Ø541 | Electrical Interlocks |  |  |  | 691.8657
| Ø542 | Kirk Key Ingterlocks |  |  |  | 76.3028
| Ø543 | Real Time Control |  |  |  | 168.768
| Ø544 | PC Link/FD/FG Changes |  |  |  | 2643.744
| Ø545 | Instrumentation |  |  |  | 577.6401
| Ø546 | Coil Protection |  |  |  | 178.7178
| Ø547 | Machine Protection System |  |  |  | 1225.0898
Ø55 | System Design & Integration |  |  |  | 612.9047
| Ø551 | System Design |  |  |  | 442.6844
| Ø552 | System Testing |  |  |  | 170.2203
ØFY09 | ActualFY09 |  |  |  | 385.771 | 385.771
|  |  |  | GRAND TOTAL | 8361.4253 | 8361.4253
Note: M&S Cost: 2242k$; Sub-contractor for Installation: 1012k$ - Included above.

## Tab C Risk and uncertainty
Cost Center: |  | 1170
Job Number: |  | 5500 (Covers elements 5200 - 5500)
Job Title: |  | NSTX Center Stack Upgrade - Power System
Job Manager: |  | S. Ramakrishnan
Uncertainty of the Estimate
|  |  | High | Medium | Low | Uncertainty Range (%) | Comments/Other Considerations
| Design Maturity |  |  | x
| Design Complexity |  |  | x
Residual Impacts
[11 empty] | Cost Impact |  | Schedule Impact
| Risk Description |  |  |  |  | Likelihood of Occurring | Mitigation Plan |  |  | Basis of estimate | Low ($K) | High ($K) | Low (weeks) | High (Weeks)
1
2
3
4
5
Notes:
(1) | Cost impacts should NOT include standing army costs which are separately calculated from the schedule impact
(2) | The schedule impacts should be entered as the min and max impacts on the critical path.
If there is no critical path impact then the schedule entries should be zero.
(3) | Likelihood of occurrence should be entered consistent with our risk classification methodology, i.e.
VL= Very Likely (P>80%), L=Likely (80%>P>40%), U=Unlikley (40%>P>10%), VU=Very Unlikely (P<10%), NC=Non-credible (P<1%)
Design Maturity Definition
High
Final design available. All design features/requirements well
known. No further design development or evolution expected that
will impact estimate.
Medium
Preliminary design available. Some additional design evolution
likely. Further developments can be somewhat expected or
anticipated and reflected in estimate.
Low
No better than conceptual design basis currently available. Design
details, procedures, etc. still need much development and
evolution of requirements beyond estimate basis is likely and
expected.
Design Complexity Definition
Low
Work is fairly well understood -- either standard construction or
repetition of activities performed in past. Little likelihood of
estimate not being well understood and requirements not being
well defined.
Medium
More complex work requirements that have potential to impact
cost and schedule estimates. Limited experience performing
similar tasks, so ability to estimate accurately is somewhat suspect
High
Extremely challenging tasks and/or requirements. Unique or firstof-
a-kind assembly or work tasks. No good basis for estimating
work exists so there is a high degree of estimate uncertainty.
Based on standard industry and DOE estimate classifications (Per AACEI Recommended